MANUFACTURE AND BILLS OF QUANTITIES

Electrical

THE TENDERERS ARE REQUESTED TO COMPLETE ALL TEMPLATES (bills of quantities)

WITH OFFERS . ALL PRICE IS WITH VA.T.

APPROVED MANUFACTURER ELECTRICAL LIST ITEM APPROVED Distribution Board a) Schneider (France) b) Eaton (Germany) Instruments and Meters a) Satec (Local) b) ABB (Europe) Disconnecting Switches a) Schneider (France) b) Eaton (Germany) Contactors, Relays &Motor Control a) Schneider (France) b) Eaton (Germany) Wires &Cables a) Synergy b) Pamukkali Data Cables& Accessories a) Daetwyler (SWISS) b) 3M (USA) Rack Cabinets& Accessories a) Daetwyler (SWISS) b) Info-Legrand c) APC (USA) Data Switches a) Cisco Catayst 2960x Computers &Servers a) Dell b) HP Cable Trays &Ladders& Floor Boxes a) OBO Bettermann (Germany) b) Nidax (Germany) Capacitor Banks a) EKJ (Germany) b) Simens (Germany) Motors &Starters a) Eaton b) Telemecanique (France) IP Telephone a) NEC b) Panasonic Boxes: a) Ave (Italy) b) Btcino (Italy) Wiring Devices: a) Legrand (France) b) Btcino Living (Italy) Cable Management: a) Legrand (France) b) Btcino (Italy) Lighting Fixtures a) Disano b) Trilux c) Thorn d) Philips Public Address &Voice Alarm System (PAVA) a) Bosch (Holland) b) TOA (Japan) Fire Alarm System a) Notifire (USA) b) Bosch c) Hochiki (Japan) FM-200 System a) Fike b) kidde Intrusion System a) Honeywell b) Bosch Queue Management System a) Wavetec CCTV System a) Bosch (Holland) b) Pelco c) Axis d) Honeywell Access Control System a) Bosch b) Honeywell Intercom System a) Aiphone (Japan) Uninterruptable Power Supply (UPS) a) Gamatronic b) APC (USA) Stand-By Generator a) Caterpillar b) Power Link c) FG-Welson BILLS OF QUANTITIES AND DESCRIPTIONS OF ELECTRICAL WORKS (BILL No. 12)

General Provisions of Electrical Works

Rates of electrical installations shall includes for:

- Electrical works including all required materials, accessories,labor, all as required according to drawings, specifications and bill of quantities.

- Cutting, and pining.

- Forming, or cutting holes, chases, channels etc.in reinforced concrete structure, block works or existing walls.

- Plugging and screwing

- Preparation of all required workshop drawings and as built drawings as specified.

- Testing electrical installations as specified including:

-Providing and personal necessary for testing.

-Providing written certificates for testing results

- Preparation of all electrical works

- Removing all unneeded electrical installations (if any) and keeping in good condition in coordination with the engineer

- All outlets, switches, cables, wires should be labeled (number and tags)

- All conduits used should be fire retardant and color coded

- All systems should have 3-years warranty

| BILL No. 12. |
| --- |
| ELECTRICAL WORKS |
| Item | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT |
| NO. |  |  |  | EURO | EURO |
| 12.1 | Underground Electrical Service Builders works: Supply, install, test and commission the following Builders work including excavation and backfilling as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements. A) 3x6" UPVC pipeS for main power lines B)4" Cobra pipe | MR MR | 20 120 |  |  |
| 12.2 | Cables and Wires 600 Volt Cables: Supply, install, test and commission 600 volts N2X cables with all required accessories for proper installation and operation conduits, cable lugs, ties.. etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements A) 3x95+50+50mm2, XLPE B) 4x35+16mm2, XLPE C)5x16mm2, XLPE D)5x10mm2, XLPE E)3x2.5mm2,XLPE Jacket Heater&Battary Charger F) 3x1.5mm2, XLPE Control | MR MR MR MR MR MR | 15 70 35 50 30 15 |  |  |
| 12.3.1 | Supporting Devices Power sockets: Supply, install, test and commission the following Power sockets as shown on drawing, the price includes ,cables (3*2.5mm2),back boxes and al other requirements as per the preamble, the specifications and supervision engineer's requirements A)16A 3-pin power socket B)16A 3-pin power socket water proof C)16A 3-pin power socket duplex D)16A 3-pin power switched socket For Air Curtain E)Hot Water Cylinder Point including isolating switch with indication lamp, cables, conduits, and all accessories F)Electrical Point for Electrical gate. G)16A 5-pin 3-phase power socket H)Trip Coil Unit | No No No No No No No No | 4 2 2 1 1 1 1 1 |  |  |
| 12.3.2 | Insolating switches: Supply, install, connect, test and commission complete with all wiring, conduits, galvanized steel trunking, boxes, isolating switch and all other accessories form the appropriate distribution board or MCC as specified and detailed on drawings for the following: A) 4P,63 insolator in WP enclosure for Refrigerator Units | No | 10 |  |  |
| 12.4.1 | Main Distribution Equipment Main Distribution Board:(MDB) Supply, install, connect, test and commission complete main distribution board including digital instruments, signal lamps, (MCCB) circuit breaker bus bars, space for cables, cable clamps/terminals, cable shoes, current transformers microprocessor metering package , that is connected to LAN directly, protection equipment, as per drawings, specifications and local electric authority requirements. A)MDB includes KWHM, ATS,Distribution | No | 1 |  |  |
| 12.4.2 | Final Distribution Boards: Supply, install, connect, testing and commission the following final distribution board, complete with (MCCB), (MCB) circuit breakers (15KA), isolators, earth leakage C.B, distribution terminal blocks according to drawings, specifications and relevant codes A)DBS B)DB-ER | No No | 1 1 |  |  |
| 12.5.1 | Lighting Lighting point: Supply, install, connect, test and commission a complete lighting point including all conductors, retardant PVC conduits, cables (3*1.5mm2,5*1.5mm2), switches , boxes, ceiling rose, fire retardant silicon flexible connection cables and all other accessories. As per drawings specifications and related standards. A)Lighting Point, through cables | No | 29 |  |  |
| 12.5.2 | Lighting Fixtures Supply, install, connect, test and commission lighting fixtures, including all supports, lamps, suspensions, clamps, switchgears, internal conductors and/or cables, and all other accessories necessary as per drawings, specifications and related standards. 1°)Type A1 2°) Type A2 3°) Type A3 4°) Type A4 | No No No No | 11 4 7 7 |  |  |
| 12.6 | Earthing Earthing System: Supply, install, connect, test and commission a complete earthing system for the project including all conductors, termination to PEC ,19 mm diameter steel copper rods, cables, clamps, conduits, handholes with heavy duty cast iron cover, fixing, etc., as per specification, drawings, local electric authority regulations, engineers approval and related codes consisting of the following: A) generator earthing that includes galvanized steel strip welded each meter to its base B)16mm2, 1" CU earthing for generator earth bus to PEC . C) 3 sets of 19mm,Dia, 1.5m L,CU rods including pits with heavy duty cast iron covers D) 6mm2 uninsulated earthing of all metal parts that includes cable trays, water pipes, cable ladder, ac units, distribution boards bodies E) PEC 40x4x0.4 mm2 in metal box/base for generator and other for building. | LS | 1 |  |  |
| 12.7.1 | Fire Alarm System Fire Alarm System Fixtures: Supply, install, connect, test and commission an addressable fire-alarm system including back-up batteries, charger, cabinet, with IP cnnection and all accessories as per drawings, specifications and related codes as following: A).1 Loop expandable intelligent addressable fire alarm control panel with network capability. The control panel must have 4 general purpose Form C relays, and eight notification appliance circuits. The controlpanel must be ULFM approved B) Addressable photo smoke detector C) Addressable heat detector D)Addressable manual call point (Break Glass) E) Sounder 6" with flasher F)Horn strobe with flasher IP54 G)Indication Lamp H)Fault Insolator I)Auto dialer J)Monitor Module (Interface between FM200 systems for MDB with main fire alarm system.) | No No No No No No No No No No | 1 1 2 2 2 1 0 1 1 1 |  |  |
| 12.7.2 | Fire Alarm System Points: Supply, install, connect, test and commission addressable fire-alarm system points including retardant conduits, 2*1mm fire resistance cables and boxes (850c) and all accessories as per drawings, specifications engineers approval and related codes . A)Fire alarm system point( smoke, heat, gas, break glass, siren, horn/strobe) B) Main connection box behind FACP | No No | 10 1 |  |  |
| 12.7.3 | FM200- System: Supply, install, connect, test and commission complete FM 200 system for MDB including smoke ,heat detectors(cross zoning) , factory filled and pressurized clean agent,SCH40 galvanized steel pipes network, with all valves and fittings, shuttle valve, pressure gauge switch, solenoid valve, safety valves, flexible hose, discharge nozzles, and all accessories as per drawings, specifications engineers approval. Note: The contractor should submit UL flow calculation report including work shop drawings from the original manufacturer. The system consisted from the following: FM200- MDB: A)Extinguishing Fire alarm control panel. B)Photo smoke detector C)Ionization smoke detector D)Manual Relese Unit E)Manual Abort Unit F)Indoor Sounder G)Discharge Nozzle H)10KG FM200 Cylinder | No No No No No No No No | 1 3 3 1 1 1 3 1 |  |  |
| 12.7.4 | Tel. System: Tel. points: Supply, install, connect, test and commission the following Telephone points including conduits,Cat6A cable, boxes, tel. sockets, as per specifications, and all accessories as per drawings, specifications engineers approval. . A)Telephone socket outlet RJ45 | No | 2 |  |  |
| 12.8 | Stand-By Systems: Stand-by Generator System: Supply ,install ,test and commission Stand-by Emergency Diesel Generator set with control panel including all equipment and accessories, as specified in the specifications. The Generator shall be 1500 rpm,50 Hz, EU stage II emissions, compliant and equipped with automatic fuel filling system, fuel gear pump, exhaust silencer, battery charger and batteries and battery rack mounted to machine base frame, water jacket heater, built in fuel tank, factory made weather and sound proof canopy, super silencer not more than 35dB,anti condensation heater for alternator, remote annunciate all controls and tools set, all cabling within the canopy, with built in RJ45 interface port for remote monitoring and management over LAN/WAN and Mod bus protocol, as per specification, and related codes and supervisor engineer. A)Stand-by Generator Set Capacity (200KVA) B)Fuel Tank 1000L capacity with all required piping, fittings and accessories needed for automatic full filling. | No No | 1 1 |  |  |
| TOTAL |  |  |

SUMMARY  OF ELECTRICAL OFFER

|  |  | TOTAL |
| --- | --- | --- |
| ITEM | DESCRIPTION | EURO |
| Bill No. 12 | Electrical Works |  |
| Grand Total |  |  |
| Percentage % discount or addition |  |  |
| Net Grand Total Include VAT |  |  |

Note: All Prices Include VAT

The sum of ……………………………………………….EURO

Contractor: ------------------------------------------------------------

Signature:   ------------------------------------------------------------

Date:           ------------------------------------------------------------